## MatrixSummary
LSE/DP Reliability Standards
Applicable to All LSE/DP | Select Applicable Standards - By Category |  |  |  | Select Applicable
Standards
|  |  | 24 Hr Real Time Monitoring & Control Capability | Responsible for Special Protection System | Standards Considered on Case by Case Criteria
| Responsible for UFLS | Responsible for UVLS |  |  |  |  | TRUE | FALSE | FALSE | FALSE
BAL-005-0 Automatic Generation Control | PRC-008-0 Underfrequency Load Shedding Equipment Maintenance Programs | PRC-010-0 Assessment of the Design and Effectiveness of UVLS Program | IRO-001-1 Reliability Coordination — Responsibilities and Authorities | PRC-015-0 Special Protection System Data and Documentation | EOP-002-2 Capacity and Energy Emergencies |  | FALSE | FALSE |  |  | FALSE
CIP-001-1 Sabotage Reporting | PRC-009-0 UFLS Performance Following an Underfrequency Event | PRC-011-0 UVLS System Maintenance and Testing | IRO-005-1 Reliability Coordination — Current Day Operations | PRC-016-0 Special Protection System Misoperations | EOP-004-1 Disturbance Reporting |  | 1 | 0 |  |  | FALSE
FAC-002-0 Coordination of Plans for New Facilities | Have UFLS Delegation Agreement | PRC-021-1 Under-Voltage Load Shedding Program Data | TOP-001-1 Reliability Responsibilities and Authorities | PRC-017-0 Special Protection System Maintenance and Testing | IRO-004-1 Reliability Coordination — Operations Planning | [5 empty] | FALSE
MOD-017-0 Aggregated Actual and Forecast Demands and Net Energy for Load |  | PRC-022-1 Under-Voltage Load Shedding Program Performance |  |  | IRO-STD-006-0 Qualified Path Unscheduled Flow Relief | [5 empty] | FALSE
MOD-018-0 Reports of Actual and Forecast Demand Data |  | Have UVLS Delegation Agreement |  |  | MOD-019-0 Forecasts of Interruptible Demands and DCLM Data | [5 empty] | FALSE
TOP-002-2 Normal Operations Planning |  |  |  |  | MOD-020-0 Providing Interruptible Demands and DCLM Data | [5 empty] | FALSE
PRC-007-0 Assuring Consistency with Regional UFLS Program Requirements |  |  |  |  | MOD-021-0 Accounting Methodology for Effects of Controllable DSM in Forecasts | [5 empty] | FALSE
[5 empty] | PRC-004-1 Analysis and Mitigation of Transmission and Generation Protection System Misoperations | [5 empty] | FALSE
[5 empty] | PRC-005-1 Transmission and Generation Protection System Maintenance and Testing | [5 empty] | TRUE
For each case by case Standard unchecked in the above matrix, select the appropriate exemption criteria from the list below:
Standard | Criteria1 | Criteria2 | Criteria3 | Criteria4
EOP-002-2 | [5 empty] | eop004 | No potential effect to the bulk power system. |  |  | iro004 | Delegated to BA | iro006 | Not applicable. | mod19 | No interruptible or DCLM. | prc004 | Delegation to BA. | spec cond | Applicable only to selected interconnection points - see attachments | eop002 | Not applicable
EOP-004-1 | No potential for loop flow | Radial, no reporting. | No generation | No potential effect to the bulk power system - see attachments. |  |  | No potential effect to the bulk power system - see attachments. |  |  |  | Delegated/handled by Coop/G&T |  | No 24 hour scheduling. | mod20 | Delegated to BA. | prc005 | No applicable transmission equipment. |  | Applicable to all transmission interconnection points.
IRO-004-1 | Will supply if requested. | [5 empty] | Radial, no reporting. |  |  |  | Will supply if requested. |  | Handled by BA. | mod21 | Delegated to Coorp/G&T
IRO-STD-006-0 | Not applicable. | No 24 hour scheduling. |  |  |  |  | No generation | [5 empty] | Delegated/handled by Coop/G&T |  | Unable to comply due to lack of SCADA.
MOD-019-0 | No interruptible or DCLM. | [5 empty] | Load too small. | [5 empty] | Will provide if requested.
MOD-020-0 | No interruptible or DCLM. | [5 empty] | Will report to BA on request.
MOD-021-0 | No interruptible or DCLM.
| Select exemption criteria OR applicable Special Conditions | [5 empty] | No potential for loop flow
| Special Conditions | Criteria1 | Criteria2 | Criteria3
PRC-004-1 |  | No applicable transmission equipment.
PRC-005-1 |  | No applicable transmission equipment.
Yes
Yes

## Apply to all LSE_DP
Following Standards are applicable to all registered Load Serving Entities and/or Distribution Providers
Standard and Title | Req. No. | Text of Requirement | LSE/DP
BAL-005-0 Automatic Generation Control | R1. | All generation, transmission, and load operating within an Interconnection must be included within the metered boundaries of a Balancing Authority Area. | LSE
| R1.3 | Each Load-Serving Entity with load operating in an Interconnection shall ensure that those loads are included within the metered boundaries of a Balancing Authority Area. | LSE
CIP-001-1 Sabotage Reporting | R1. | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load Serving Entity shall have procedures for the recognition of and for making their operating personnel aware of sabotage events on its facilities and multi-site sabotage affecting larger portions of the Interconnection. | LSE
| R2. | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load Serving Entity shall have procedures for the communication of information concerning sabotage events to appropriate parties in the Interconnection. | LSE
| R3. | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load Serving Entity shall provide its operating personnel with sabotage response guidelines, including personnel to contact, for reporting disturbances due to sabotage events. | LSE
| R4. | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load Serving Entity shall establish communications contacts, as applicable, with local Federal Bureau of Investigation (FBI) or Royal Canadian Mounted Police (RCMP) officials and develop reporting procedures as appropriate to their circumstances. | LSE
FAC-002-0 Coordination of Plans for New Facilities | R1. | The Generator Owner, Transmission Owner, Distribution Provider, and Load-Serving Entity seeking to integrate generation facilities, transmission facilities, and electricity end-user facilities shall each coordinate and cooperate on its assessments with its Transmission Planner and Planning Authority. The assessment shall include: | LSE/DP
| R1.1 | Evaluation of the reliability impact of the new facilities and their connections on the interconnected transmission systems. | LSE/DP
| R1.2 | Ensurance of compliance with NERC Reliability Standards and applicable Regional, subregional, Power Pool, and individual system planning criteria and facility connection requirements. | LSE/DP
| R1.3 | Evidence that the parties involved in the assessment have coordinated and cooperated on the assessment of the reliability impacts of new facilities on the interconnected transmission systems. While these studies may be performed independently, the results shall be jointly evaluated and coordinated by the entities involved. | LSE/DP
| R1.4 | Evidence that the assessment included steady-state, short-circuit, and dynamics studies as necessary to evaluate system performance in accordance with Reliability Standard TPL-001-0. | LSE/DP
| R1.5 | Documentation that the assessment included study assumptions, system performance, alternatives considered, and jointly coordinated recommendations. | LSE/DP
| R2. | The Planning Authority, Transmission Planner, Generator Owner, Transmission Owner, Load-Serving Entity, and Distribution Provider shall each retain its documentation (of its evaluation of the reliability impact of the new facilities and their connections on the interconnected transmission systems) for three years and shall provide the documentation to the Regional Reliability Organization(s) and NERC on request (within 30 calendar days). | LSE/DP
MOD-017-0 Aggregated Actual and Forecast Demands and Net Energy for Load | R1. | The Load-Serving Entity, Planning Authority and Resource Planner shall each provide the following information annually on an aggregated Regional, subregional, Power Pool, individual system, or Load-Serving Entity basis to NERC, the Regional Reliability Organizations, and any other entities specified by the documentation in Standard MOD-016-1_R1. | LSE
| R1.1 | Integrated hourly demands in megawatts (MW) for the prior year. | LSE
| R1.2 | Monthly and annual peak hour actual demands in MW and Net Energy for Load in gigawatthours (GWh) for the prior year. | LSE
| R1.3 | Monthly peak hour forecast demands in MW and Net Energy for Load in GWh for the next two years. | LSE
| R1.4 | Annual Peak hour forecast demands (summer and winter) in MW and annual Net Energy for load in GWh for at least five years and up to ten years into the future, as requested. | LSE
MOD-018-0 Reports of Actual and Forecast Demand Data | R1. | The Load-Serving Entity, Planning Authority, Transmission Planner and Resource Planner’s report of actual and forecast demand data (reported on either an aggregated or dispersed basis) shall: | LSE
| R1.1 | Indicate whether the demand data of nonmember entities within an area or Regional Reliability Organization are included, and | LSE
| R1.2 | Address assumptions, methods, and the manner in which uncertainties are treated in the forecasts of aggregated peak demands and Net Energy for Load. | LSE
| R1.3 | Items (MOD-018-0_R1.1) and (MOD-018-0_R1.2) shall be addressed as described in the reporting procedures developed for Standard MOD-016-0_R1. | LSE
| R2. | The Load-Serving Entity, Planning Authority, Transmission Planner and Resource Planner shall each report data associated with Reliability Standard MOD-018-0_R1 to NERC, the Regional Reliability Organization, Load-Serving Entity, Planning Authority, and Resource Planner on request (within 30 calendar days). | LSE
TOP-002-2 Normal Operations Planning | R3. | Each Load Serving Entity and Generator Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal operations with its Host Balancing Authority and Transmission Service Provider. Each Balancing Authority and Transmission Service Provider shall coordinate its current-day, next-day, and seasonal operations with its Transmission Operator. | LSE
| R18. | Neighboring Balancing Authorities, Transmission Operators, Generator Operators, Transmission Service Providers and Load Serving Entities shall use uniform line identifiers when referring to transmission facilities of an interconnected network. | LSE
PRC-007-0 Assuring Consistency with Regional UFLS Program Requirements | R1. | The Transmission Owner and Distribution Provider, with a UFLS program (as required by its Regional Reliability Organization) shall ensure that its UFLS program is consistent with its Regional Reliability Organization’s UFLS program requirements. | DP
| R2. | The Transmission Owner, Transmission Operator, Distribution Provider, and Load-Serving Entity that owns or operates a UFLS program (as required by its Regional Reliability Organization) shall provide, and annually update, its underfrequency data as necessary for its Regional Reliability Organization to maintain and update a UFLS program database. | LSE/DP
| R3. | The Transmission Owner and Distribution Provider that owns a UFLS program (as required by its Regional Reliability Organization) shall provide its documentation of that UFLS program to its Regional Reliability Organization on request (30 calendar days). | DP
WECC Intent for PRC-007-0 Compliance |  | The intent of the WECC Coordinated Off-Nominal Frequency Load Shedding and Restoration Plan is to have all load within the Western Interconnection considered in the program. To clarify compliance obligations under standard PRC-007-0, the LSE/DP must be able to demonstrate that 1) its load is included in its own UFLS program or 2) its load is included in another entity’s program. All other applicable elements of the requirements must also be met.

## UFLS Responsibility
Following Standards are applicable to LSE/DPs designated as the responsible entity for underfrequency load shedding program designed to protect the bulk power system.
Standard and Title | Req. No. | Text of Requirement | LSE/DP
PRC-008-0 Underfrequency Load Shedding Equipment Maintenance Programs | R1. | The Transmission Owner and Distribution Provider with a UFLS program (as required by its Regional Reliability Organization) shall have a UFLS equipment maintenance and testing program in place. This UFLS equipment maintenance and testing program shall include UFLS equipment identification, the schedule for UFLS equipment testing, and the schedule for UFLS equipment maintenance. | DP
| R2. | The Transmission Owner and Distribution Provider with a UFLS program (as required by its Regional Reliability Organization) shall implement its UFLS equipment maintenance and testing program and shall provide UFLS maintenance and testing program results to its Regional Reliability Organization and NERC on request (within 30 calendar days). | DP
PRC-009-0 UFLS Performance Following an Underfrequency Event | R1. | The Transmission Owner, Transmission Operator, Load-Serving Entity and Distribution Provider that owns or operates a UFLS program (as required by its Regional Reliability Organization) shall analyze and document its UFLS program performance in accordance with its Regional Reliability Organization’s UFLS program. The analysis shall address the performance of UFLS equipment and program effectiveness following system events resulting in system frequency excursions below the initializing set points of the UFLS program. The analysis shall include, but not be limited to: | LSE/DP
| R1.1 | A description of the event including initiating conditions. | LSE/DP
| R1.2 | A review of the UFLS set points and tripping times. | LSE/DP
| R1.3 | A simulation of the event. | LSE/DP
| R1.4 | A summary of the findings. | LSE/DP
| R2. | The Transmission Owner, Transmission Operator, Load-Serving Entity, and Distribution Provider that owns or operates a UFLS program (as required by its Regional Reliability Organization) shall provide documentation of the analysis of the UFLS program to its Regional Reliability Organization and NERC on request 90 calendar days after the system event. | LSE/DP | 1
0

## UVLS Responsibility
Following Standards are applicable to LSE/DPs designated as the responsible entity for undervoltage load shedding program designed to protect the bulk power system. |  |  |  | 0
0
Standard and Title | Req. No. | Text of Requirement | LSE/DP
PRC-010-0 Assessment of the Design and Effectiveness of UVLS Program | R1. | The Load-Serving Entity, Transmission Owner, Transmission Operator, and Distribution Provider that owns or operates a UVLS program shall periodically (at least every five years or as required by changes in system conditions) conduct and document an assessment of the effectiveness of the UVLS program. This assessment shall be conducted with the associated Transmission Planner(s) and Planning Authority(ies). | LSE/DP
| R1.1 | This assessment shall include, but is not limited to: | LSE/DP
| R1.1.1 | Coordination of the UVLS programs with other protection and control systems in the Region and with other Regional Reliability Organizations, as appropriate. | LSE/DP
| R1.1.2 | Simulations that demonstrate that the UVLS programs performance is consistent with Reliability Standards TPL-001-0, TPL-002-0, TPL-003-0 and TPL-004-0. | LSE/DP
| R1.1.3 | A review of the voltage set points and timing. | LSE/DP
| R2. | The Load-Serving Entity, Transmission Owner, Transmission Operator, and Distribution Provider that owns or operates a UVLS program shall provide documentation of its current UVLS program assessment to its Regional Reliability Organization and NERC on request (30 calendar days). | LSE/DP
PRC-011-0 UVLS System Maintenance and Testing | R1. | The Transmission Owner and Distribution Provider that owns a UVLS system shall have a UVLS equipment maintenance and testing program in place. This program shall include: | DP
| R1.1 | The UVLS system identification which shall include but is not limited to: | DP
| R1.1.1 | Relays. | DP
| R1.1.2 | Instrument transformers. | DP
| R1.1.3 | Communications systems, where appropriate. | DP
| R1.1.4 | Batteries. | DP
| R1.2 | Documentation of maintenance and testing intervals and their basis. | DP
| R1.3 | Summary of testing procedure. | DP
| R1.4 | Schedule for system testing. | DP
| R1.5 | Schedule for system maintenance. | DP
| R1.6 | Date last tested/maintained. | DP
| R2. | The Transmission Owner and Distribution Provider that owns a UVLS system shall provide documentation of its UVLS equipment maintenance and testing program and the implementation of that UVLS equipment maintenance and testing program to its Regional Reliability Organization and NERC on request (within 30 calendar days). | DP
PRC-021-1 Under-Voltage Load Shedding Program Data | R1. | Each Transmission Owner and Distribution Provider that owns a UVLS program to mitigate the risk of voltage collapse or voltage instability in the BES shall annually update its UVLS data to support the Regional UVLS program database. The following data shall be provided to the Regional Reliability Organization for each installed UVLS system: | DP
| R1.1 | Size and location of customer load, or percent of connected load, to be interrupted. | DP
| R1.2 | Corresponding voltage set points and overall scheme clearing times. | DP
| R1.3 | Time delay from initiation to trip signal. | DP
| R1.4 | Breaker operating times. | DP
| R1.5 | Any other schemes that are part of or impact the UVLS programs such as related generation protection, islanding schemes, automatic load restoration schemes, UFLS and Special Protection Systems. | DP
| R2. | Each Transmission Owner and Distribution Provider that owns a UVLS program shall provide its UVLS program data to the Regional Reliability Organization within 30 calendar days of a request. | DP
PRC-022-1 Under-Voltage Load Shedding Program Performance | R1. | Each Transmission Operator, Load-Serving Entity, and Distribution Provider that operates a UVLS program to mitigate the risk of voltage collapse or voltage instability in the BES shall analyze and document all UVLS operations and Misoperations. The analysis shall include: | LSE/DP
| R1.1 | A description of the event including initiating conditions. | LSE/DP
| R1.2 | A review of the UVLS set points and tripping times. | LSE/DP
| R1.3 | A simulation of the event, if deemed appropriate by the Regional Reliability Organization. For most events, analysis of sequence of events may be sufficient and dynamic simulations may not be needed. | LSE/DP
| R1.4 | A summary of the findings. | LSE/DP
| R1.5 | For any Misoperation, a Corrective Action Plan to avoid future Misoperations of a similar nature. | LSE/DP
| R2. | Each Transmission Operator, Load-Serving Entity, and Distribution Provider that operates a UVLS program shall provide documentation of its analysis of UVLS program performance to its Regional Reliability Organization within 90 calendar days of a request. | LSE/DP

## 24 Hr
Following Standards are applicable to LSE/DPs who have 24 hour real time monitoring and control capabilities. |  |  |  | 0
Standard and Title | Req. No. | Text of Requirement | LSE/DP
IRO-001-1 Reliability Coordination — Responsibilities and Authorities | R8. | Transmission Operators, Balancing Authorities, Generator Operators, Transmission Service Providers, Load-Serving Entities, and Purchasing-Selling Entities shall comply with Reliability Coordinator directives unless such actions would violate safety, equipment, or regulatory or statutory requirements. Under these circumstances, the Transmission Operator, Balancing Authority, Generator Operator, Transmission Service Provider, Load-Serving Entity, or Purchasing-Selling Entity shall immediately inform the Reliability Coordinator of the inability to perform the directive so that the Reliability Coordinator may implement alternate remedial actions. | LSE
IRO-005-1 Reliability Coordination — Current Day Operations | R13. | Each Reliability Coordinator shall ensure that all Transmission Operators, Balancing Authorities, Generator Operators, Transmission Service Providers, Load-Serving Entities, and Purchasing-Selling Entities operate to prevent the likelihood that a disturbance, action, or nonaction in its Reliability Coordinator Area will result in a SOL or IROL violation in another area of the Interconnection. In instances where there is a difference in derived limits, the Reliability Coordinator and its Transmission Operators, Balancing Authorities, Generator Operators, Transmission Service Providers, Load-Serving Entities, and Purchasing-Selling Entities shall always operate the Bulk Electric System to the most limiting parameter. | LSE
TOP-001-1 Reliability Responsibilities and Authorities | R4. | Each Distribution Provider and Load Serving Entity shall comply with all reliability directives issued by the Transmission Operator, including shedding firm load, unless such actions would violate safety, equipment, regulatory or statutory requirements. Under these circumstances, the Distribution Provider or Load Serving Entity shall immediately inform the Transmission Operator of the inability to perform the directive so that the Transmission Operator can implement alternate remedial actions. | LSE/DP

## SPS
Following Standards are applicable to LSE/DPs designated as the responsible entity for undervoltage load shedding program designed to protect the bulk power system. |  |  |  | 0
Standard and Title | Req. No. | Text of Requirement | LSE/DP
PRC-015-0 Special Protection System Data and Documentation | R1. | The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall maintain a list of and provide data for existing and proposed SPSs as specified in Reliability Standard PRC-013-0_R1. | DP
| R2. | The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall have evidence it reviewed new or functionally modified SPSs in accordance with the Regional Reliability Organization’s procedures as defined in Reliability Standard PRC-012-0_R1 prior to being placed in service. | DP
| R3. | The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall provide documentation of SPS data and the results of Studies that show compliance of new or functionally modified SPSs with NERC Reliability Standards and Regional Reliability Organization criteria to affected Regional Reliability Organizations and NERC on request (within 30 calendar days). | DP
PRC-016-0 Special Protection System Misoperations | R1. | The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall analyze its SPS operations and maintain a record of all misoperations in accordance with the Regional SPS review procedure specified in Reliability Standard PRC-012-0_R1. | DP
| R2. | The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall take corrective actions to avoid future misoperations. | DP
| R3. | The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall provide documentation of the misoperation analyses and the corrective action plans to its Regional Reliability Organization and NERC on request (within 90 calendar days). | DP
PRC-017-0 Special Protection System Maintenance and Testing | R1. | The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall have a system maintenance and testing program(s) in place. The program(s) shall include: | DP
| R1.1 | SPS identification shall include but is not limited to: | DP
| R1.1.1 | Relays. | DP
| R1.1.2 | Instrument transformers. | DP
| R1.1.3 | Communications systems, where appropriate. | DP
| R1.1.4 | Batteries. | DP
| R1.2 | Documentation of maintenance and testing intervals and their basis. | DP
| R1.3 | Summary of testing procedure. | DP
| R1.4 | Schedule for system testing. | DP
| R1.5 | Schedule for system maintenance. | DP
| R1.6 | Date last tested/maintained. | DP
| R2. | The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall provide documentation of the program and its implementation to the appropriate Regional Reliability Organizations and NERC on request (within 30 calendar days). | DP

## Case by Case
Review each Standard and check if applicable. If not, provide criteria on Matrix Summary page.
Standard and Title | Req. No. | Text of Requirement | LSE/DP | Additional explanation on exemption criteria
EOP-002-2 Capacity and Energy Emergnecies | R9 | R9. When a Transmission Service Provider expects to elevate the transmission service priority of an Interchange Transaction from Priority 6 (Network IntegrationTransmission Service from Non-designated Resources) to Priority 7 (Network Integration Transmission Service from designated Network Resources) as permitted in its transmission tariff (See Attachment 1-IRO-006-0 “Transmission Loading Relief Procedure” for explanation of Transmission Service Priorities): |  |  | 0
| R9.1 | R9.1. The deficient Load-Serving Entity shall request its Reliability Coordinator toinitiate an Energy Emergency Alert in accordance with Attachment 1-EOP002-0. | LSE |  | 0
EOP-004-1 Disturbance Reporting | R2. | A Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator or Load Serving Entity shall promptly analyze Bulk Electric System disturbances on its system or facilities. | LSE |  | 0
| R3. | A Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator or Load Serving Entity experiencing a reportable incident shall provide a preliminary written report to its Regional Reliability Organization and NERC. | LSE |  | 0
| R3.1 | The affected Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator or Load Serving Entity shall submit within 24 hours of the disturbance or unusual occurrence either a copy of the report submitted to DOE, or, if no DOE report is required, a copy of the NERC Interconnection Reliability Operating Limit and Preliminary Disturbance Report form. Events that are not identified until some time after they occur shall be reported within 24 hours of being recognized. | LSE |  | 0
| R3.2 | Applicable reporting forms are provided in Attachments 1-EOP-004 and 2-EOP-004. | LSE |  | 0
| R3.3 | Under certain adverse conditions, e.g., severe weather, it may not be possible to assess the damage caused by a disturbance and issue a written Interconnection Reliability Operating Limit and Preliminary Disturbance Report within 24 hours. In such cases, the affected Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, or Load Serving Entity shall promptly notify its Regional Reliability Organization(s) and NERC, and verbally provide as much information as is available at that time. The affected Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, or Load Serving Entity shall then provide timely, periodic verbal updates until adequate information is available to issue a written Preliminary Disturbance Report. | LSE |  | 0
| R3.4 | If, in the judgment of the Regional Reliability Organization, after consultation with the Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, or Load Serving Entity in which a disturbance occurred, a final report is required, the affected Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, or Load Serving Entity shall prepare this report within 60 days. As a minimum, the final report shall have a discussion of the events and its cause, the conclusions reached, and recommendations to prevent recurrence of this type of event. The report shall be subject to Regional Reliability Organization approval. | LSE |  | 0
IRO-004-1 Reliability Coordination — Operations Planning | R4. | Each Transmission Operator, Balancing Authority, Transmission Owner, Generator Owner, Generator Operator, and Load-Serving Entity in the Reliability Coordinator Area shall provide information required for system studies, such as critical facility status, Load, generation, operating reserve projections, and known Interchange Transactions. This information shall be available by 1200 Central Standard Time for the Eastern Interconnection and 1200 Pacific Standard Time for the Western Interconnection. | LSE |  | 1
IRO-STD-006-0 Qualified Path Unscheduled Flow Relief | WR1. | Curtailment of Contributing Schedules WECC’s Unscheduled Flow Mitigation Plan (Plan), which is on file with FERC and has been accepted by FERC (most recently prior to the date hereof on November 20, 2001 in Docket No. ER01-3085-000), 1/ specifies that members2/ shall comply with requests from (Qualified) Transfer Path Operators to take actions that will reduce unscheduled flow on the Qualified Path in accordance with the table entitled “WECC Unscheduled Flow Procedure Summary of Curtailment Actions,” which is located in Attachment 1 of the Plan. Plan Section 11: 11.1 When USF Accommodation, as specified in Section 7, together with coordinated operation of the Qualified Controllable Devices, as specified in Section 9, are insufficient to reduce the Actual Flow on the Qualified Transfer Path to below the Transfer Limit, the Transfer Path Operator shall request curtailments in Schedules that contribute to the USF through the Qualified Transfer Path according to the USF Reduction Procedure. 11.2 Responsible Entities shall comply in a timely manner with a Transfer Path Operator's request for Schedule Curtailments. Plan Attachment 1 Section 9: “h. Upon receipt of a curtailment request, Contributing Schedules which are subject to curtailments will be reduced (or equivalent alternative schedule adjustments will be effected) in accordance with the following procedures: i. Receivers of Contributing Schedules will initiate the requested schedule reductions unless an otherwise agreed upon procedure for schedule reduction achieving the equivalent effect on the Qualified Transfer Path is established by the Receiver and/or the Sender. ii. Responsible Entities may arrange among themselves to make curtailments called for by this USF Reduction Procedure in a manner other than prescribed provided that the arrangements are as effective as the identified schedule curtailment in reducing USF across the Qualified Transfer Path. Responsible Entities may make bilateral arrangements, which will enable a Responsible Entity with schedules on the affected Qualified Transfer Path to make the required curtailments in lieu of making larger curtailments in schedules over other parallel paths. Where alternative schedule adjustments are utilized, it is the Receiver's responsibility to cause schedule adjustments to be effected which provide the same reduction in flow across the Qualified Transfer Path as would have been achieved by the prescribed reduction in the Contributing Schedule. iii. The total amount of requested schedule reduction may be apportioned to the applicable schedules at the discretion of the Receiver subject to item iv below. iv. Irrespective of the schedules altered or the manner in which they are altered, each Responsible Entity's overall net reduction in Actual Flow across the constrained Qualified Transfer Path must be equivalent to or greater than the reduction which would have been achieved had the identified schedule reduction occurred as requested. v. System dispatchers or real-time schedulers should identify in advance those schedules that qualify for curtailment requests for all Qualified Transfer Paths. This will expedite implementation of this USF Reduction Procedure when requested. vi. While this USF Reduction Procedure does not expect receivers to curtail schedules which would result in loss of firm load, nothing in this USF Reduction Procedure shall relieve the receiver of the obligation to achieve the required reduction in USF across the constrained Qualified Transfer Path.” Contributing Schedule curtailments apply to schedules in place before initiation of the USF Procedure at Step 4 (First level Contributing Schedule Curtailment) or higher step. At the time a Step 4 Level 1 USF Action or higher step is initiated, Schedules are established by the existence of an “Implemented” NERC Transaction Tag. Restricted Transactions After the USF Event is declared, a transaction with greater than a 5% Transfer Distribution Factor (TDF) on the Qualified Path in the qualified direction will be considered a “Restricted Transaction.” Changes to Restricted Transactions, other than the specific curtailments used to comply with relief obligations, cannot be made unless some alternative action is taken to compensate for the full impact on the Qualified Path. This applies to: New transaction, and Extensions or Adjustments to existing transaction.” If two or more Qualified Paths become simultaneously constrained to the point where the curtailment of contributing schedules is necessary, schedule curtailments which relieve USF on one path but increase USF on any other curtailed path shall not be made, unless specific procedures or methods are provided to address this condition. The entity shall be compliant with this standard although the required curtailments were not made. | LSE
MOD-019-0 Forecasts of Interruptible Demands and DCLM Data | R1. | The Load-Serving Entity, Planning Authority, Transmission Planner, and Resource Planner shall each provide annually its forecasts of interruptible demands and Direct Control Load Management (DCLM) data for at least five years and up to ten years into the future, as requested, for summer and winter peak system conditions to NERC, the Regional Reliability Organizations, and other entities (Load-Serving Entities, Planning Authorities, and Resource Planners) as specified by the documentation in Reliability Standard MOD-016-1_R1. | LSE
MOD-020-0 Providing Interruptible Demands and DCLM Data | R1. | The Load-Serving Entity, Transmission Planner, and Resource Planner shall each make known its amount of interruptible demands and Direct Control Load Management (DCLM) to Transmission Operators, Balancing Authorities, and Reliability Coordinators on request within 30 calendar days. | LSE
MOD-021-0 Accounting Methodology for Effects of Controllable DSM in Forecasts | R1. | The Load-Serving Entity Transmission Planner and Resource Planner’s forecasts shall each clearly document how the Demand and energy effects of DSM programs (such as conservation, time-of-use rates, interruptible Demands, and Direct Control Load Management) are addressed. | LSE
| R2. | The Load-Serving Entity, Transmission Planner and Resource Planner shall each include information detailing how Demand-Side Management measures are addressed in the forecasts of its Peak Demand and annual Net Energy for Load in the data reporting procedures of Standard MOD-016-0_R1. | LSE
| R3. | The Load-Serving Entity, Transmission Planner and Resource Planner shall each make documentation on the treatment of its DSM programs available to NERC on request (within 30 calendar days). | LSE
PRC-004-1 Analysis and Mitigation of Transmission and Generation Protection System Misoperations | R1. | The Transmission Owner and any Distribution Provider that owns a transmission Protection System shall each analyze its transmission Protection System Misoperations and shall develop and implement a Corrective Action Plan to avoid future Misoperations of a similar nature according to the Regional Reliability Organization’s procedures developed for Reliability Standard PRC-003 Requirement 1. | DP
| R3. | The Transmission Owner, any Distribution Provider that owns a transmission Protection System, and the Generator Owner shall each provide to its Regional Reliability Organization, documentation of its Misoperations analyses and Corrective Action Plans according to the Regional Reliability Organization’s procedures developed for PRC-003 R1. | DP
PRC-005-1 Transmission and Generation Protection System Maintenance and Testing | R1. | Each Transmission Owner and any Distribution Provider that owns a transmission Protection System and each Generator Owner that owns a generation Protection System shall have a Protection System maintenance and testing program for Protection Systems that affect the reliability of the BES. The program shall include: | DP
| R1.1 | Maintenance and testing intervals and their basis. | DP
| R1.2 | Summary of maintenance and testing procedures. | DP
| R2. | Each Transmission Owner and any Distribution Provider that owns a transmission Protection System and each Generator Owner that owns a generation Protection System shall provide documentation of its Protection System maintenance and testing program and the implementation of that program to its Regional Reliability Organization on request (within 30 calendar days). The documentation of the program implementation shall include: | DP
| R2.1 | Evidence Protection System devices were maintained and tested within the defined intervals. | DP
| R2.2 | Date each Protection System device was last tested/maintained. | DP

## All Req List
LSE/DP Reliability Standards
Standard and Title | Req. No. | Text of Requirement | LSE/DP | Applicable to All LSE/DP | Responsible for UFLS | Responsible for UVLS | 24 Hr Real Time Monitoring & Control Capability | Responsible for Special Protection System | Standards Considered on Case by Case Criteria
BAL-005-0 Automatic Generation Control | R1. | All generation, transmission, and load operating within an Interconnection must be included within the metered boundaries of a Balancing Authority Area. | LSE | X
| R1.3 | Each Load-Serving Entity with load operating in an Interconnection shall ensure that those loads are included within the metered boundaries of a Balancing Authority Area. | LSE | X
CIP-001-1 Sabotage Reporting | R1. | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load Serving Entity shall have procedures for the recognition of and for making their operating personnel aware of sabotage events on its facilities and multi-site sabotage affecting larger portions of the Interconnection. | LSE | X
| R2. | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load Serving Entity shall have procedures for the communication of information concerning sabotage events to appropriate parties in the Interconnection. | LSE | X
| R3. | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load Serving Entity shall provide its operating personnel with sabotage response guidelines, including personnel to contact, for reporting disturbances due to sabotage events. | LSE | X
| R4. | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load Serving Entity shall establish communications contacts, as applicable, with local Federal Bureau of Investigation (FBI) or Royal Canadian Mounted Police (RCMP) officials and develop reporting procedures as appropriate to their circumstances. | LSE | X
EOP-002-2 Capacity and Energy Emergnecies | R9 | R9. When a Transmission Service Provider expects to elevate the transmission service priority of an Interchange Transaction from Priority 6 (Network IntegrationTransmission Service from Non-designated Resources) to Priority 7 (Network Integration Transmission Service from designated Network Resources) as permitted in its transmission tariff (See Attachment 1-IRO-006-0 “Transmission Loading Relief Procedure” for explanation of Transmission Service Priorities):
| R9.1 | R9.1. The deficient Load-Serving Entity shall request its Reliability Coordinator toinitiate an Energy Emergency Alert in accordance with Attachment 1-EOP002-0. | LSE | [5 empty] | X
EOP-004-1 Disturbance Reporting | R2. | A Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator or Load Serving Entity shall promptly analyze Bulk Electric System disturbances on its system or facilities. | LSE | [5 empty] | X
| R3. | A Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator or Load Serving Entity experiencing a reportable incident shall provide a preliminary written report to its Regional Reliability Organization and NERC. | LSE | [5 empty] | X
| R3.1 | The affected Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator or Load Serving Entity shall submit within 24 hours of the disturbance or unusual occurrence either a copy of the report submitted to DOE, or, if no DOE report is required, a copy of the NERC Interconnection Reliability Operating Limit and Preliminary Disturbance Report form. Events that are not identified until some time after they occur shall be reported within 24 hours of being recognized. | LSE | [5 empty] | X
| R3.2 | Applicable reporting forms are provided in Attachments 1-EOP-004 and 2-EOP-004. | LSE | [5 empty] | X
| R3.3 | Under certain adverse conditions, e.g., severe weather, it may not be possible to assess the damage caused by a disturbance and issue a written Interconnection Reliability Operating Limit and Preliminary Disturbance Report within 24 hours. In such cases, the affected Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, or Load Serving Entity shall promptly notify its Regional Reliability Organization(s) and NERC, and verbally provide as much information as is available at that time. The affected Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, or Load Serving Entity shall then provide timely, periodic verbal updates until adequate information is available to issue a written Preliminary Disturbance Report. | LSE | [5 empty] | X
| R3.4 | If, in the judgment of the Regional Reliability Organization, after consultation with the Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, or Load Serving Entity in which a disturbance occurred, a final report is required, the affected Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, or Load Serving Entity shall prepare this report within 60 days. As a minimum, the final report shall have a discussion of the events and its cause, the conclusions reached, and recommendations to prevent recurrence of this type of event. The report shall be subject to Regional Reliability Organization approval. | LSE | [5 empty] | X
FAC-002-0 Coordination of Plans for New Facilities | R1. | The Generator Owner, Transmission Owner, Distribution Provider, and Load-Serving Entity seeking to integrate generation facilities, transmission facilities, and electricity end-user facilities shall each coordinate and cooperate on its assessments with its Transmission Planner and Planning Authority. The assessment shall include: | LSE/DP | X
| R1.1 | Evaluation of the reliability impact of the new facilities and their connections on the interconnected transmission systems. | LSE/DP | X
| R1.2 | Ensurance of compliance with NERC Reliability Standards and applicable Regional, subregional, Power Pool, and individual system planning criteria and facility connection requirements. | LSE/DP | X
| R1.3 | Evidence that the parties involved in the assessment have coordinated and cooperated on the assessment of the reliability impacts of new facilities on the interconnected transmission systems. While these studies may be performed independently, the results shall be jointly evaluated and coordinated by the entities involved. | LSE/DP | X
| R1.4 | Evidence that the assessment included steady-state, short-circuit, and dynamics studies as necessary to evaluate system performance in accordance with Reliability Standard TPL-001-0. | LSE/DP | X
| R1.5 | Documentation that the assessment included study assumptions, system performance, alternatives considered, and jointly coordinated recommendations. | LSE/DP | X
| R2. | The Planning Authority, Transmission Planner, Generator Owner, Transmission Owner, Load-Serving Entity, and Distribution Provider shall each retain its documentation (of its evaluation of the reliability impact of the new facilities and their connections on the interconnected transmission systems) for three years and shall provide the documentation to the Regional Reliability Organization(s) and NERC on request (within 30 calendar days). | LSE/DP | X
IRO-001-1 Reliability Coordination — Responsibilities and Authorities | R8. | Transmission Operators, Balancing Authorities, Generator Operators, Transmission Service Providers, Load-Serving Entities, and Purchasing-Selling Entities shall comply with Reliability Coordinator directives unless such actions would violate safety, equipment, or regulatory or statutory requirements. Under these circumstances, the Transmission Operator, Balancing Authority, Generator Operator, Transmission Service Provider, Load-Serving Entity, or Purchasing-Selling Entity shall immediately inform the Reliability Coordinator of the inability to perform the directive so that the Reliability Coordinator may implement alternate remedial actions. | LSE |  |  |  | X
IRO-004-1 Reliability Coordination — Operations Planning | R4. | Each Transmission Operator, Balancing Authority, Transmission Owner, Generator Owner, Generator Operator, and Load-Serving Entity in the Reliability Coordinator Area shall provide information required for system studies, such as critical facility status, Load, generation, operating reserve projections, and known Interchange Transactions. This information shall be available by 1200 Central Standard Time for the Eastern Interconnection and 1200 Pacific Standard Time for the Western Interconnection. | LSE | [5 empty] | X
IRO-005-1 Reliability Coordination — Current Day Operations | R13. | Each Reliability Coordinator shall ensure that all Transmission Operators, Balancing Authorities, Generator Operators, Transmission Service Providers, Load-Serving Entities, and Purchasing-Selling Entities operate to prevent the likelihood that a disturbance, action, or nonaction in its Reliability Coordinator Area will result in a SOL or IROL violation in another area of the Interconnection. In instances where there is a difference in derived limits, the Reliability Coordinator and its Transmission Operators, Balancing Authorities, Generator Operators, Transmission Service Providers, Load-Serving Entities, and Purchasing-Selling Entities shall always operate the Bulk Electric System to the most limiting parameter. | LSE |  |  |  | X
IRO-STD-006-0 Qualified Path Unscheduled Flow Relief | WR1. | Curtailment of Contributing Schedules WECC’s Unscheduled Flow Mitigation Plan (Plan), which is on file with FERC and has been accepted by FERC (most recently prior to the date hereof on November 20, 2001 in Docket No. ER01-3085-000), 1/ specifies that members2/ shall comply with requests from (Qualified) Transfer Path Operators to take actions that will reduce unscheduled flow on the Qualified Path in accordance with the table entitled “WECC Unscheduled Flow Procedure Summary of Curtailment Actions,” which is located in Attachment 1 of the Plan. Plan Section 11: 11.1 When USF Accommodation, as specified in Section 7, together with coordinated operation of the Qualified Controllable Devices, as specified in Section 9, are insufficient to reduce the Actual Flow on the Qualified Transfer Path to below the Transfer Limit, the Transfer Path Operator shall request curtailments in Schedules that contribute to the USF through the Qualified Transfer Path according to the USF Reduction Procedure. 11.2 Responsible Entities shall comply in a timely manner with a Transfer Path Operator's request for Schedule Curtailments. Plan Attachment 1 Section 9: “h. Upon receipt of a curtailment request, Contributing Schedules which are subject to curtailments will be reduced (or equivalent alternative schedule adjustments will be effected) in accordance with the following procedures: i. Receivers of Contributing Schedules will initiate the requested schedule reductions unless an otherwise agreed upon procedure for schedule reduction achieving the equivalent effect on the Qualified Transfer Path is established by the Receiver and/or the Sender. ii. Responsible Entities may arrange among themselves to make curtailments called for by this USF Reduction Procedure in a manner other than prescribed provided that the arrangements are as effective as the identified schedule curtailment in reducing USF across the Qualified Transfer Path. Responsible Entities may make bilateral arrangements, which will enable a Responsible Entity with schedules on the affected Qualified Transfer Path to make the required curtailments in lieu of making larger curtailments in schedules over other parallel paths. Where alternative schedule adjustments are utilized, it is the Receiver's responsibility to cause schedule adjustments to be effected which provide the same reduction in flow across the Qualified Transfer Path as would have been achieved by the prescribed reduction in the Contributing Schedule. iii. The total amount of requested schedule reduction may be apportioned to the applicable schedules at the discretion of the Receiver subject to item iv below. iv. Irrespective of the schedules altered or the manner in which they are altered, each Responsible Entity's overall net reduction in Actual Flow across the constrained Qualified Transfer Path must be equivalent to or greater than the reduction which would have been achieved had the identified schedule reduction occurred as requested. v. System dispatchers or real-time schedulers should identify in advance those schedules that qualify for curtailment requests for all Qualified Transfer Paths. This will expedite implementation of this USF Reduction Procedure when requested. vi. While this USF Reduction Procedure does not expect receivers to curtail schedules which would result in loss of firm load, nothing in this USF Reduction Procedure shall relieve the receiver of the obligation to achieve the required reduction in USF across the constrained Qualified Transfer Path.” Contributing Schedule curtailments apply to schedules in place before initiation of the USF Procedure at Step 4 (First level Contributing Schedule Curtailment) or higher step. At the time a Step 4 Level 1 USF Action or higher step is initiated, Schedules are established by the existence of an “Implemented” NERC Transaction Tag. Restricted Transactions After the USF Event is declared, a transaction with greater than a 5% Transfer Distribution Factor (TDF) on the Qualified Path in the qualified direction will be considered a “Restricted Transaction.” Changes to Restricted Transactions, other than the specific curtailments used to comply with relief obligations, cannot be made unless some alternative action is taken to compensate for the full impact on the Qualified Path. This applies to: New transaction, and Extensions or Adjustments to existing transaction.” If two or more Qualified Paths become simultaneously constrained to the point where the curtailment of contributing schedules is necessary, schedule curtailments which relieve USF on one path but increase USF on any other curtailed path shall not be made, unless specific procedures or methods are provided to address this condition. The entity shall be compliant with this standard although the required curtailments were not made. | LSE | [5 empty] | X
MOD-017-0 Aggregated Actual and Forecast Demands and Net Energy for Load | R1. | The Load-Serving Entity, Planning Authority and Resource Planner shall each provide the following information annually on an aggregated Regional, subregional, Power Pool, individual system, or Load-Serving Entity basis to NERC, the Regional Reliability Organizations, and any other entities specified by the documentation in Standard MOD-016-1_R1. | LSE | X
| R1.1 | Integrated hourly demands in megawatts (MW) for the prior year. | LSE | X
| R1.2 | Monthly and annual peak hour actual demands in MW and Net Energy for Load in gigawatthours (GWh) for the prior year. | LSE | X
| R1.3 | Monthly peak hour forecast demands in MW and Net Energy for Load in GWh for the next two years. | LSE | X
| R1.4 | Annual Peak hour forecast demands (summer and winter) in MW and annual Net Energy for load in GWh for at least five years and up to ten years into the future, as requested. | LSE | X
MOD-018-0 Reports of Actual and Forecast Demand Data | R1. | The Load-Serving Entity, Planning Authority, Transmission Planner and Resource Planner’s report of actual and forecast demand data (reported on either an aggregated or dispersed basis) shall: | LSE | X
| R1.1 | Indicate whether the demand data of nonmember entities within an area or Regional Reliability Organization are included, and | LSE | X
| R1.2 | Address assumptions, methods, and the manner in which uncertainties are treated in the forecasts of aggregated peak demands and Net Energy for Load. | LSE | X
| R1.3 | Items (MOD-018-0_R1.1) and (MOD-018-0_R1.2) shall be addressed as described in the reporting procedures developed for Standard MOD-016-0_R1. | LSE | X
| R2. | The Load-Serving Entity, Planning Authority, Transmission Planner and Resource Planner shall each report data associated with Reliability Standard MOD-018-0_R1 to NERC, the Regional Reliability Organization, Load-Serving Entity, Planning Authority, and Resource Planner on request (within 30 calendar days). | LSE | X
MOD-019-0 Forecasts of Interruptible Demands and DCLM Data | R1. | The Load-Serving Entity, Planning Authority, Transmission Planner, and Resource Planner shall each provide annually its forecasts of interruptible demands and Direct Control Load Management (DCLM) data for at least five years and up to ten years into the future, as requested, for summer and winter peak system conditions to NERC, the Regional Reliability Organizations, and other entities (Load-Serving Entities, Planning Authorities, and Resource Planners) as specified by the documentation in Reliability Standard MOD-016-1_R1. | LSE | [5 empty] | X
MOD-020-0 Providing Interruptible Demands and DCLM Data | R1. | The Load-Serving Entity, Transmission Planner, and Resource Planner shall each make known its amount of interruptible demands and Direct Control Load Management (DCLM) to Transmission Operators, Balancing Authorities, and Reliability Coordinators on request within 30 calendar days. | LSE | [5 empty] | X
MOD-021-0 Accounting Methodology for Effects of Controllable DSM in Forecasts | R1. | The Load-Serving Entity Transmission Planner and Resource Planner’s forecasts shall each clearly document how the Demand and energy effects of DSM programs (such as conservation, time-of-use rates, interruptible Demands, and Direct Control Load Management) are addressed. | LSE | [5 empty] | X
| R2. | The Load-Serving Entity, Transmission Planner and Resource Planner shall each include information detailing how Demand-Side Management measures are addressed in the forecasts of its Peak Demand and annual Net Energy for Load in the data reporting procedures of Standard MOD-016-0_R1. | LSE | [5 empty] | X
| R3. | The Load-Serving Entity, Transmission Planner and Resource Planner shall each make documentation on the treatment of its DSM programs available to NERC on request (within 30 calendar days). | LSE | [5 empty] | X
PRC-004-1 Analysis and Mitigation of Transmission and Generation Protection System Misoperations | R1. | The Transmission Owner and any Distribution Provider that owns a transmission Protection System shall each analyze its transmission Protection System Misoperations and shall develop and implement a Corrective Action Plan to avoid future Misoperations of a similar nature according to the Regional Reliability Organization’s procedures developed for Reliability Standard PRC-003 Requirement 1. | DP | [5 empty] | X
| R3. | The Transmission Owner, any Distribution Provider that owns a transmission Protection System, and the Generator Owner shall each provide to its Regional Reliability Organization, documentation of its Misoperations analyses and Corrective Action Plans according to the Regional Reliability Organization’s procedures developed for PRC-003 R1. | DP | [5 empty] | X
PRC-005-1 Transmission and Generation Protection System Maintenance and Testing | R1. | Each Transmission Owner and any Distribution Provider that owns a transmission Protection System and each Generator Owner that owns a generation Protection System shall have a Protection System maintenance and testing program for Protection Systems that affect the reliability of the BES. The program shall include: | DP | [5 empty] | X
| R1.1 | Maintenance and testing intervals and their basis. | DP | [5 empty] | X
| R1.2 | Summary of maintenance and testing procedures. | DP | [5 empty] | X
| R2. | Each Transmission Owner and any Distribution Provider that owns a transmission Protection System and each Generator Owner that owns a generation Protection System shall provide documentation of its Protection System maintenance and testing program and the implementation of that program to its Regional Reliability Organization on request (within 30 calendar days). The documentation of the program implementation shall include: | DP | [5 empty] | X
| R2.1 | Evidence Protection System devices were maintained and tested within the defined intervals. | DP | [5 empty] | X
| R2.2 | Date each Protection System device was last tested/maintained. | DP | [5 empty] | X
PRC-007-0 Assuring Consistency with Regional UFLS Program Requirements | R1. | The Transmission Owner and Distribution Provider, with a UFLS program (as required by its Regional Reliability Organization) shall ensure that its UFLS program is consistent with its Regional Reliability Organization’s UFLS program requirements. | DP | X
| R2. | The Transmission Owner, Transmission Operator, Distribution Provider, and Load-Serving Entity that owns or operates a UFLS program (as required by its Regional Reliability Organization) shall provide, and annually update, its underfrequency data as necessary for its Regional Reliability Organization to maintain and update a UFLS program database. | LSE/DP | X
| R3. | The Transmission Owner and Distribution Provider that owns a UFLS program (as required by its Regional Reliability Organization) shall provide its documentation of that UFLS program to its Regional Reliability Organization on request (30 calendar days). | DP | X
PRC-008-0 Underfrequency Load Shedding Equipment Maintenance Programs | R1. | The Transmission Owner and Distribution Provider with a UFLS program (as required by its Regional Reliability Organization) shall have a UFLS equipment maintenance and testing program in place. This UFLS equipment maintenance and testing program shall include UFLS equipment identification, the schedule for UFLS equipment testing, and the schedule for UFLS equipment maintenance. | DP |  | X
| R2. | The Transmission Owner and Distribution Provider with a UFLS program (as required by its Regional Reliability Organization) shall implement its UFLS equipment maintenance and testing program and shall provide UFLS maintenance and testing program results to its Regional Reliability Organization and NERC on request (within 30 calendar days). | DP |  | X
PRC-009-0 UFLS Performance Following an Underfrequency Event | R1. | The Transmission Owner, Transmission Operator, Load-Serving Entity and Distribution Provider that owns or operates a UFLS program (as required by its Regional Reliability Organization) shall analyze and document its UFLS program performance in accordance with its Regional Reliability Organization’s UFLS program. The analysis shall address the performance of UFLS equipment and program effectiveness following system events resulting in system frequency excursions below the initializing set points of the UFLS program. The analysis shall include, but not be limited to: | LSE/DP |  | X
| R1.1 | A description of the event including initiating conditions. | LSE/DP |  | X
| R1.2 | A review of the UFLS set points and tripping times. | LSE/DP |  | X
| R1.3 | A simulation of the event. | LSE/DP |  | X
| R1.4 | A summary of the findings. | LSE/DP |  | X
| R2. | The Transmission Owner, Transmission Operator, Load-Serving Entity, and Distribution Provider that owns or operates a UFLS program (as required by its Regional Reliability Organization) shall provide documentation of the analysis of the UFLS program to its Regional Reliability Organization and NERC on request 90 calendar days after the system event. | LSE/DP |  | X
PRC-010-0 Assessment of the Design and Effectiveness of UVLS Program | R1. | The Load-Serving Entity, Transmission Owner, Transmission Operator, and Distribution Provider that owns or operates a UVLS program shall periodically (at least every five years or as required by changes in system conditions) conduct and document an assessment of the effectiveness of the UVLS program. This assessment shall be conducted with the associated Transmission Planner(s) and Planning Authority(ies). | LSE/DP |  |  | X
| R1.1 | This assessment shall include, but is not limited to: | LSE/DP |  |  | X
| R1.1.1 | Coordination of the UVLS programs with other protection and control systems in the Region and with other Regional Reliability Organizations, as appropriate. | LSE/DP |  |  | X
| R1.1.2 | Simulations that demonstrate that the UVLS programs performance is consistent with Reliability Standards TPL-001-0, TPL-002-0, TPL-003-0 and TPL-004-0. | LSE/DP |  |  | X
| R1.1.3 | A review of the voltage set points and timing. | LSE/DP |  |  | X
| R2. | The Load-Serving Entity, Transmission Owner, Transmission Operator, and Distribution Provider that owns or operates a UVLS program shall provide documentation of its current UVLS program assessment to its Regional Reliability Organization and NERC on request (30 calendar days). | LSE/DP |  |  | X
PRC-011-0 UVLS System Maintenance and Testing | R1. | The Transmission Owner and Distribution Provider that owns a UVLS system shall have a UVLS equipment maintenance and testing program in place. This program shall include: | DP |  |  | X
| R1.1 | The UVLS system identification which shall include but is not limited to: | DP |  |  | X
| R1.1.1 | Relays. | DP |  |  | X
| R1.1.2 | Instrument transformers. | DP |  |  | X
| R1.1.3 | Communications systems, where appropriate. | DP |  |  | X
| R1.1.4 | Batteries. | DP |  |  | X
| R1.2 | Documentation of maintenance and testing intervals and their basis. | DP |  |  | X
| R1.3 | Summary of testing procedure. | DP |  |  | X
| R1.4 | Schedule for system testing. | DP |  |  | X
| R1.5 | Schedule for system maintenance. | DP |  |  | X
| R1.6 | Date last tested/maintained. | DP |  |  | X
| R2. | The Transmission Owner and Distribution Provider that owns a UVLS system shall provide documentation of its UVLS equipment maintenance and testing program and the implementation of that UVLS equipment maintenance and testing program to its Regional Reliability Organization and NERC on request (within 30 calendar days). | DP |  |  | X
PRC-015-0 Special Protection System Data and Documentation | R1. | The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall maintain a list of and provide data for existing and proposed SPSs as specified in Reliability Standard PRC-013-0_R1. | DP |  |  |  |  | X
| R2. | The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall have evidence it reviewed new or functionally modified SPSs in accordance with the Regional Reliability Organization’s procedures as defined in Reliability Standard PRC-012-0_R1 prior to being placed in service. | DP |  |  |  |  | X
| R3. | The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall provide documentation of SPS data and the results of Studies that show compliance of new or functionally modified SPSs with NERC Reliability Standards and Regional Reliability Organization criteria to affected Regional Reliability Organizations and NERC on request (within 30 calendar days). | DP |  |  |  |  | X
PRC-016-0 Special Protection System Misoperations | R1. | The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall analyze its SPS operations and maintain a record of all misoperations in accordance with the Regional SPS review procedure specified in Reliability Standard PRC-012-0_R1. | DP |  |  |  |  | X
| R2. | The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall take corrective actions to avoid future misoperations. | DP |  |  |  |  | X
| R3. | The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall provide documentation of the misoperation analyses and the corrective action plans to its Regional Reliability Organization and NERC on request (within 90 calendar days). | DP |  |  |  |  | X
PRC-017-0 Special Protection System Maintenance and Testing | R1. | The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall have a system maintenance and testing program(s) in place. The program(s) shall include: | DP |  |  |  |  | X
| R1.1 | SPS identification shall include but is not limited to: | DP |  |  |  |  | X
| R1.1.1 | Relays. | DP |  |  |  |  | X
| R1.1.2 | Instrument transformers. | DP |  |  |  |  | X
| R1.1.3 | Communications systems, where appropriate. | DP |  |  |  |  | X
| R1.1.4 | Batteries. | DP |  |  |  |  | X
| R1.2 | Documentation of maintenance and testing intervals and their basis. | DP |  |  |  |  | X
| R1.3 | Summary of testing procedure. | DP |  |  |  |  | X
| R1.4 | Schedule for system testing. | DP |  |  |  |  | X
| R1.5 | Schedule for system maintenance. | DP |  |  |  |  | X
| R1.6 | Date last tested/maintained. | DP |  |  |  |  | X
| R2. | The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall provide documentation of the program and its implementation to the appropriate Regional Reliability Organizations and NERC on request (within 30 calendar days). | DP |  |  |  |  | X
PRC-021-1 Under-Voltage Load Shedding Program Data | R1. | Each Transmission Owner and Distribution Provider that owns a UVLS program to mitigate the risk of voltage collapse or voltage instability in the BES shall annually update its UVLS data to support the Regional UVLS program database. The following data shall be provided to the Regional Reliability Organization for each installed UVLS system: | DP |  |  | X
| R1.1 | Size and location of customer load, or percent of connected load, to be interrupted. | DP |  |  | X
| R1.2 | Corresponding voltage set points and overall scheme clearing times. | DP |  |  | X
| R1.3 | Time delay from initiation to trip signal. | DP |  |  | X
| R1.4 | Breaker operating times. | DP |  |  | X
| R1.5 | Any other schemes that are part of or impact the UVLS programs such as related generation protection, islanding schemes, automatic load restoration schemes, UFLS and Special Protection Systems. | DP |  |  | X
| R2. | Each Transmission Owner and Distribution Provider that owns a UVLS program shall provide its UVLS program data to the Regional Reliability Organization within 30 calendar days of a request. | DP |  |  | X
PRC-022-1 Under-Voltage Load Shedding Program Performance | R1. | Each Transmission Operator, Load-Serving Entity, and Distribution Provider that operates a UVLS program to mitigate the risk of voltage collapse or voltage instability in the BES shall analyze and document all UVLS operations and Misoperations. The analysis shall include: | LSE/DP |  |  | X
| R1.1 | A description of the event including initiating conditions. | LSE/DP |  |  | X
| R1.2 | A review of the UVLS set points and tripping times. | LSE/DP |  |  | X
| R1.3 | A simulation of the event, if deemed appropriate by the Regional Reliability Organization. For most events, analysis of sequence of events may be sufficient and dynamic simulations may not be needed. | LSE/DP |  |  | X
| R1.4 | A summary of the findings. | LSE/DP |  |  | X
| R1.5 | For any Misoperation, a Corrective Action Plan to avoid future Misoperations of a similar nature. | LSE/DP |  |  | X
| R2. | Each Transmission Operator, Load-Serving Entity, and Distribution Provider that operates a UVLS program shall provide documentation of its analysis of UVLS program performance to its Regional Reliability Organization within 90 calendar days of a request. | LSE/DP |  |  | X
TOP-001-1 Reliability Responsibilities and Authorities | R4. | Each Distribution Provider and Load Serving Entity shall comply with all reliability directives issued by the Transmission Operator, including shedding firm load, unless such actions would violate safety, equipment, regulatory or statutory requirements. Under these circumstances, the Distribution Provider or Load Serving Entity shall immediately inform the Transmission Operator of the inability to perform the directive so that the Transmission Operator can implement alternate remedial actions. | LSE/DP |  |  |  | X
TOP-002-2 Normal Operations Planning | R3. | Each Load Serving Entity and Generator Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal operations with its Host Balancing Authority and Transmission Service Provider. Each Balancing Authority and Transmission Service Provider shall coordinate its current-day, next-day, and seasonal operations with its Transmission Operator. | LSE | X
| R18. | Neighboring Balancing Authorities, Transmission Operators, Generator Operators, Transmission Service Providers and Load Serving Entities shall use uniform line identifiers when referring to transmission facilities of an interconnected network. | LSE | X